{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":8,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAA-DW1P-H"]
[]
[]
[]
[]
["","","","","","EWAA011DAW1P-H-","EWAA014DAW1P-H-","EWAA016DAW1P-H-"]
["Äänenpaineen taso","Jäähdytys","","Nimell.","dBA","47.7","50.8","51.0"]
["Hydrauliikkakomponentit","Paisuntasäiliö","","Tilavuus","l","8","8","8"]
["Toimintalämpötila-alue","Ilma","Jäähdytys","Min.","°CDB","10","10","10"]
["","","","Maks.","°CDB","43","43","43"]
["","Vesipuoli","Jäähdytys","Maks.","°CDB","22","22","22"]
["","","","Min.","°CDB","5","5","5"]
["Kylmäainemäärä","Per piiri","","","kg","3.80","3.80","3.80"]
["","Refrigerant charge-=-Per circuit-=-TCO2Eq","","","TCO2Eq","2.6","2.6","2.6"]
["Kompressori","Tyyppi","","","","Hermeettisesti suljettu taajuusmuuttaja swing-kompressori","Hermeettisesti suljettu taajuusmuuttaja swing-kompressori","Hermeettisesti suljettu taajuusmuuttaja swing-kompressori"]
["","Starting method","","","","Taajuusmuuttajakäyttöinen","Taajuusmuuttajakäyttöinen","Taajuusmuuttajakäyttöinen"]
["","Määrä_","","","","1","1","1"]
["Lauhdutin","Tyyppi","","","","Tehokas rivoitettu rivoitettu putki ja integroitu lisäjäähdytin","Tehokas rivoitettu rivoitettu putki ja integroitu lisäjäähdytin","Tehokas rivoitettu rivoitettu putki ja integroitu lisäjäähdytin"]
["Paino","Yksikkö","","","kg","147","147","147"]
["EER","","","","","3.26 (1), 5.31 (2)","3.16 (1), 5.04 (2)","3.06 (1), 4.74 (2)"]
["Kylmäaine","GWP","","","","675.0","675.0","675.0"]
["","Tyyppi","","","","R-32","R-32","R-32"]
["","Piirit","","Määrä","","1","1","1"]
["","Ohjaus","","","","Elektroninen paisuntaventtiili","Elektroninen paisuntaventtiili","Elektroninen paisuntaventtiili"]
["Puhallinmoottori","Nopeus","Jäähdytys","Nimell.","r/min","550","650","650"]
["Jäähdytysteho","Nimell.","","","kW","11.6 (1), 11.5 (2)","12.8 (1), 12.7 (2)","14.0 (1), 15.3 (2)"]
["Höyrystin","Vesitilavuus","","","l","2","2","2"]
["","Järjestelmän vedentilavuus vähintään","","","l","20 (6)","20 (6)","20 (6)"]
["","Tyyppi","","","","Levylämmönvaihdin","Levylämmönvaihdin","Levylämmönvaihdin"]
["Ottoteho","Jäähdytys","","Nimell.","kW","3.56 (1), 2.17 (2)","4.06 (1), 2.51 (2)","4.58 (1), 3.24 (2)"]
["Äänen tehotaso","Jäähdytys","","Nimell.","dBA","67.0","69.0","69.0"]
["Mitat","Yksikkö","","Leveys","mm","1,380","1,380","1,380"]
["","","","Syvyys","mm","460","460","460"]
["","","","Korkeus","mm","870","870","870"]
["Tehonsäätö","Menetelmä","","","","Muuttuva (invertteri)","Muuttuva (invertteri)","Muuttuva (invertteri)"]
["Puhallin","Ilmamäärä","Jäähdytys","Nimell.","m³/min","70","85","85"]
["Kompressori","Starting method","","","","Taajuusmuuttaja","Taajuusmuuttaja","Taajuusmuuttaja"]
["Power supply","Vaihe","","","","3~","3~","3~"]
["","Taajuus","","","Hz","50","50","50"]
["","Nimi","","","","W1","W1","W1"]
["","Jännite","","","V","400","400","400"]
["Huomautukset","","","","","(1) - Jäähdytys: EW 12°C; LW 7°C; ympäristön lämpötila: 35°CDB","(1) - Jäähdytys: EW 12°C; LW 7°C; ympäristön lämpötila: 35°CDB","(1) - Jäähdytys: EW 12°C; LW 7°C; ympäristön lämpötila: 35°CDB"]
["","","","","","(2) - Jäähdytys: EW 23°C; LW 18°C; ympäristön lämpötila: 35°CDB","(2) - Jäähdytys: EW 23°C; LW 18°C; ympäristön lämpötila: 35°CDB","(2) - Jäähdytys: EW 23°C; LW 18°C; ympäristön lämpötila: 35°CDB"]
["","","","","","(3) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - EN14825 mukaisesti","(5) - EN14825 mukaisesti","(5) - EN14825 mukaisesti"]
["","","","","","(6) - Toimintatilan mukaan, katso asennusohjetta.","(6) - Toimintatilan mukaan, katso asennusohjetta.","(6) - Toimintatilan mukaan, katso asennusohjetta."]
["","","","","","(7) - Lisätietoja on toimintalämpötila-alueen piirroksessa","(7) - Lisätietoja on toimintalämpötila-alueen piirroksessa","(7) - Lisätietoja on toimintalämpötila-alueen piirroksessa"]