{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":28,"n_cols":17,"rows_kept":28,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWS-DZXE"]
[]
[]
[]
[]
["","","","","EWWS340DZXEA1","EWWS470DZXEA1","EWWS570DZXEA1","EWWS670DZXEA2","EWWS680DZXEA2","EWWS740DZXEA1","EWWS950DZXEA2","EWWSC10DZXEA3","EWWSC11DZXEA2","EWWSC14DZXEA3","EWWSC15DZXEA2","EWWSC17DZXEA3","EWWSC22DZXEA3"]
["Jäähdytysteho","Nimell.","","kW","337","471","558","671","674","729","942","1,025","1,117","1,420","1,451","1,653","2,129"]
["Tehonsäätö","Menetelmä","","","Muuttuva","Muuttuva","Muuttuva","Muuttuva","Muuttuva","Muuttuva","Muuttuva","Muuttuva","Muuttuva","Muuttuva","Muuttuva","Muuttuva","Muuttuva"]
["","Vähimmäisteho","","%","29","20","20","15","15","17","10","10","10","7","9","7","6"]
["Ottoteho","Jäähdytys","Nimell.","kW","70.2","95.1","108","139","139","129","188","209","215","287","259","324","385"]
["EER","","","","4.8","4.96","5.15","4.8","4.85","5.61","5.01","4.89","5.18","4.94","5.6","5.1","5.52"]
["ESEER","","","","0","0","0","0","0","0","0","0","0","0","0","0","0"]
["Mitat","Yksikkö","Syvyys","mm","3,625","3,625","3,625","3,625","3,585","3,585","3,585","4,688","3,580","4,793","3,580","4,768","4,812"]
["","","Korkeus","mm","1,865","1,865","1,865","1,985","1,985","1,985","1,985","2,082","2,200","2,083","2,200","2,225","2,290"]
["","","Leveys","mm","1,055","1,055","1,055","1,160","1,160","1,160","1,160","1,510","1,270","1,510","1,270","1,510","1,510"]
["Paino","Yksikkö","","kg","1,750","1,950","2,050","2,850","2,850","2,650","3,000","4,400","3,700","4,700","3,900","5,100","5,900"]
["","Paino käyttökunnossa","","kg","2,033","2,276","2,407","3,197","3,354","3,162","3,568","4,970","4,412","5,370","4,699","5,890","6,920"]
["Höyrystin - haihdutin","Tyyppi","","","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin","Märkä putkihöyrystin"]
["","Vesitilavuus","","l","70","96","107","107","134","134","156","207","199","272","229","317","444"]
["Höyrystin - lauhdutin","Tyyppi","","","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki","Upotettu vaippa ja Putki"]
["Kompressori","Tyyppi","","","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori","Öljytön ruuvikompressori"]
["","Määrä_","","","1","1","1","2","2","1","2","3","2","3","2","3","3"]
["Sound power level","Jäähdytys","Nimell.","dBA","87.9","88.9","89.9","91.1","91.0","91.1","92.0","92.6","93.3","93.5","94.3","94.8","95.8"]
["Äänenpaineen taso","Jäähdytys","Nimell.","dBA","69.6","70.6","71.6","72.6","72.6","72.6","73.6","73","74.6","73.9","75.6","75.2","76.2"]
["Kylmäaine","Tyyppi","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["","Täytösmäärä","","kg","160","130","130","200","200","190","200","270","250","270","250","300","355"]
["","Piirit","Määrä","","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["","GWP","","","631","631","631","631","631","631","631","631","631","631","631","631","631"]