{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":52,"n_cols":12,"rows_kept":52,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWWS-J-SS"]
[]
[]
[]
[]
["","","","","","EWWS120J-SS","EWWS140J-SS","EWWS150J-SS","EWWS180J-SS","EWWS210J-SS","EWWS240J-SS","EWWS270J-SS"]
["Jäähdytysteho","Nimell.","","","kW","115.2","136.3","154.7","180.6","207.3","241","272.2"]
["Tehonsäätö","Menetelmä","","","","Portaaton","Portaaton","Portaaton","Portaaton","Portaaton","Portaaton","Portaaton"]
["","Vähimmäisteho","","","%","25","25","25","25","25","25","25"]
["Ottoteho","Jäähdytys","","Nimell.","kW","30","36.3","41.7","47.8","54.2","65.7","74.4"]
["EER","","","","","3.85","3.75","3.72","3.78","3.82","3.67","3.66"]
["IPLV","","","","","4.1","4.11","4.09","4.11","4.12","4.64","4.59"]
["SEER","","","","","3.36","3.38","3.32","3.4","3.39","3.87","3.82"]
["Mitat","Yksikkö","","Syvyys","mm","2684","2684","2684","2684","2684","2684","2684"]
["","","","Korkeus","mm","1020","1020","1020","1020","1020","1020","1020"]
["","","","Leveys","mm","913","913","913","913","913","913","913"]
["Paino","Paino käyttökunnossa","","","kg","1211","1276","1378","1415","1473","1663","1675"]
["","Yksikkö","","","kg","1177","1233","1334","1366","1416","1600","1607"]
["Kotelo","Väri","","","","Norsunluunvalkoinen","Norsunluunvalkoinen","Norsunluunvalkoinen","Norsunluunvalkoinen","Norsunluunvalkoinen","Norsunluunvalkoinen","Norsunluunvalkoinen"]
["","Materiaali","","","","Maalattu galvanoitu teräslevy","Maalattu galvanoitu teräslevy","Maalattu galvanoitu teräslevy","Maalattu galvanoitu teräslevy","Maalattu galvanoitu teräslevy","Maalattu galvanoitu teräslevy","Maalattu galvanoitu teräslevy"]
["Höyrystin - haihdutin","Tyyppi","","","","Levylämmönvaihdin","Levylämmönvaihdin","Levylämmönvaihdin","Levylämmönvaihdin","Levylämmönvaihdin","Levylämmönvaihdin","Levylämmönvaihdin"]
["","Vesitilavuus","","","l","14","18","14","17","20","26","26"]
["Veden lämmönvaihdin - höyrystin","Veden painehäviö","Jäähdytys","Nim.","kPa","17.1","16.8","32.8","33.4","31.8","27.9","34.8"]
["Kompressori","Määrä_","","","","1","1","1","1","1","1","1"]
["","Tyyppi","","","","Yksiruuvikompressori","Yksiruuvikompressori","Yksiruuvikompressori","Yksiruuvikompressori","Yksiruuvikompressori","Yksiruuvikompressori","Yksiruuvikompressori"]
["","Käynnistysmenetelmä_","","","","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta","Wye-Delta"]
["Toimintalämpötila-alue","Vesipuoli","Höyrystin","Min.","°CDB","-10","-10","-10","-10","-10","-10","-10"]
["","","","Maks.","°CDB","15","15","15","15","15","15","15"]
["Äänen tehotaso","Jäähdytys","","Nimell.","dBA","95","95","95","95","95","95","95"]
["Äänenpaineen taso","Jäähdytys","","Nimell.","dBA","79","79","79","79","79","79","79"]
["Kylmäaine","Tyyppi","","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["","GWP","","","","629.5","629.5","629.5","629.5","629.5","629.5","629.5"]
["","Täytösmäärä","","","kg","18","35","34","37","37","38","38"]
["","Piirit","","Määrä","","1","1","1","1","1","1","1"]
["Putkikoot","Höyrystimen veden tulo/lähtö (ulkoh.)","","","","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm","76.2 mm"]
["Energiatehokkuusalue","","","","","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F","Space Heating A+++ ~ D, Water Heating A+ ~ F"]
["Virransyöttö","Vaihe","","","","3~","3~","3~","3~","3~","3~","3~"]
["Syöttöjännite","Taajuus","","","Hz","50","50","50","50","50","50","50"]
["","Jännite","","","V","400","400","400","400","400","400","400"]
["","Jännitealue","","Min.","%","-10","-10","-10","-10","-10","-10","-10"]
["","","","Maks.","%","10","10","10","10","10","10","10"]
["Yks.","Käynnistysvirta","","Maks","A","154","154","198","198","198","291","291"]
["","Virta käynnissä","Jäähdytys","Nim.","A","50","60","70","78","87","105","117"]
["Yksikkö","Virta käynnissä","","Maks","A","81","96","108","122","141","164","185"]
["","Yksikön enimmäisvirta kaapelien kokomääritystä varten","","","A","89","107","120","136","158","183","207"]
["Huomautukset","","","","","(1) - Jäähdytys: EW 12°C; LW 7°C; ympäristön lämpötila: 35°CDB","(1) - Jäähdytys: EW 12°C; LW 7°C; ympäristön lämpötila: 35°CDB","(1) - Jäähdytys: EW 12°C; LW 7°C; ympäristön lämpötila: 35°CDB","(1) - Jäähdytys: EW 12°C; LW 7°C; ympäristön lämpötila: 35°CDB","(1) - Jäähdytys: EW 12°C; LW 7°C; ympäristön lämpötila: 35°CDB","(1) - Jäähdytys: EW 12°C; LW 7°C; ympäristön lämpötila: 35°CDB","(1) - Jäähdytys: EW 12°C; LW 7°C; ympäristön lämpötila: 35°CDB"]
["","","","","","(2) - Jäähdytys: EW 23°C; LW 18°C; ympäristön lämpötila: 35°CDB","(2) - Jäähdytys: EW 23°C; LW 18°C; ympäristön lämpötila: 35°CDB","(2) - Jäähdytys: EW 23°C; LW 18°C; ympäristön lämpötila: 35°CDB","(2) - Jäähdytys: EW 23°C; LW 18°C; ympäristön lämpötila: 35°CDB","(2) - Jäähdytys: EW 23°C; LW 18°C; ympäristön lämpötila: 35°CDB","(2) - Jäähdytys: EW 23°C; LW 18°C; ympäristön lämpötila: 35°CDB","(2) - Jäähdytys: EW 23°C; LW 18°C; ympäristön lämpötila: 35°CDB"]
["","","","","","(3) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)","(3) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 35°C (DT = 5°C)"]
["","","","","","(4) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)","(4) - Olosuhteet: Ta DB/WB 7°C/6°C - LWC 45°C (Dt=5°C)"]
["","","","","","(5) - EN14825 mukaisesti","(5) - EN14825 mukaisesti","(5) - EN14825 mukaisesti","(5) - EN14825 mukaisesti","(5) - EN14825 mukaisesti","(5) - EN14825 mukaisesti","(5) - EN14825 mukaisesti"]
["","","","","","(6) - Toimintatilan mukaan, katso asennusohjetta.","(6) - Toimintatilan mukaan, katso asennusohjetta.","(6) - Toimintatilan mukaan, katso asennusohjetta.","(6) - Toimintatilan mukaan, katso asennusohjetta.","(6) - Toimintatilan mukaan, katso asennusohjetta.","(6) - Toimintatilan mukaan, katso asennusohjetta.","(6) - Toimintatilan mukaan, katso asennusohjetta."]
["","","","","","(7) - Lisätietoja on toimintalämpötila-alueen piirroksessa","(7) - Lisätietoja on toimintalämpötila-alueen piirroksessa","(7) - Lisätietoja on toimintalämpötila-alueen piirroksessa","(7) - Lisätietoja on toimintalämpötila-alueen piirroksessa","(7) - Lisätietoja on toimintalämpötila-alueen piirroksessa","(7) - Lisätietoja on toimintalämpötila-alueen piirroksessa","(7) - Lisätietoja on toimintalämpötila-alueen piirroksessa"]