{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":53,"n_cols":6,"rows_kept":53,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWYK-QZ"]
[]
[]
[]
[]
["","","","","","EWYK135QZXSA2"]
["Jäähdytysteho","Nimell.","","","kW","128.30"]
["Tehonsäätö","Menetelmä","","","","Invertteriohjattu"]
["","Vähimmäisteho","","","%","11"]
["Ottoteho","Jäähdytys","","Nimell.","kW","48.42"]
["EER","","","","","2.65"]
["IPLV","","","","","5.94"]
["SEER","","","","","4.81"]
["Mitat","Yksikkö","","Syvyys","mm","1207"]
["","","","Korkeus","mm","2382"]
["","","","Leveys","mm","2653"]
["Paino","Paino käyttökunnossa","","","kg","1272"]
["","Yksikkö","","","kg","1239"]
["Kotelo","Väri","","","","Norsunluunvalkoinen"]
["","Materiaali","","","","Maalattu galvanoitu teräslevy"]
["Lauhdutin","Tyyppi","","","","Al rivat ja Cu putket"]
["Puhallin","Määrä","","","","2"]
["","Tyyppi","","","","Aksiaalinen"]
["","Ilmanvirtaus","Jäähdytys","Nim.","l/s","141160"]
["Puhallinmoottori","Käyttö","","","","Harjaton"]
["Kompressori","Määrä_","","","","2"]
["","Tyyppi","","","","Scroll"]
["Toimintalämpötila-alue","Ilma","Jäähdytys","Min.","°CDB","-20"]
["","","","Maks.","°CDB","46"]
["","Vesipuoli","Höyrystin","Min.","°CDB","20"]
["","","","Maks.","°CDB","75"]
["Äänen tehotaso","Jäähdytys","","Nimell.","dBA","90.9"]
["Äänenpaineen taso","Jäähdytys","","Nimell.","dBA","72.7"]
["Kylmäaine","Tyyppi","","","","R-290"]
["","GWP","","","","0.02"]
["","Täytösmäärä","","","kg","6.6"]
["","Piirit","","Määrä","","2"]
["Putkikoot","Höyrystimen veden tulo/lähtö (ulkoh.)","","","","3\""]
["Virransyöttö","Vaihe","","","","3"]
["Syöttöjännite","Taajuus","","","Hz","50"]
["","Jännite","","","V","400"]
["","Jännitealue","","Min.","%","-10"]
["","","","Maks.","%","10"]
["Yks.","Käynnistysvirta","","Maks","A","0"]
["","Virta käynnissä","Jäähdytys","Nim.","A","80.9"]
["Yksikkö","Virta käynnissä","","Maks","A","128.0"]
["","Yksikön enimmäisvirta kaapelien kokomääritystä varten","","","A","141.1"]
["Huomautukset","","","","","(1) - Jäähdytys: höyrystimen tulevan veden lämpötila 12℃; höyrystimen poistuvan veden lämpötila 7℃, ympäristön lämpötila 35℃"]
["","","","","","(2) - Olosuhteet: ulkolämpötila 7°CDB, 6°CWB; LWC 35°C (DT = 5°C)"]
["","","","","","(3) - EN14825 mukaisesti"]
["","","","","","(4) - Toimintatilan mukaan, katso asennusohjetta."]
["","","","","","(5) - Lisätietoja on toimintalämpötila-alueen piirroksessa"]
["","","","","","(6) - Performance data calculated as Chiller Configurator - 2.0.0"]