{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":8,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-B"]
[]
[]
[]
[]
["","","","","","RZAG35B5V1B","RZAG50B5V1B","RZAG60B5V1B"]
["Mitat","Yksikkö","","Korkeus","mm","734","734","734"]
["","","","Leveys","mm","870","870","870"]
["","","","Syvyys","mm","373","373","373"]
["Paino","Yksikkö","","","kg","52","52","52"]
["Kompressori","Type","","","","Hermeettisesti suljettu swing-kompressori","Hermeettisesti suljettu swing-kompressori","Hermeettisesti suljettu swing-kompressori"]
["Toimintalämpötila-alue","Jäähdytys","Ympäristö","Min.","°CDB","-20","-20","-20"]
["","","","Maks.","°CDB","52","52","52"]
["","Lämmitys","Ympäristö","Min.","°CWB","-21","-21","-21"]
["","","","Maks.","°CWB","18","18","18"]
["Äänen tehotaso","Jäähdytys","","","dBA","62","63","64"]
["","Lämmitys","","","dBA","62","63","64"]
["Äänenpaineen taso","Jäähdytys","","Nimell.","dBA","48","49","50"]
["","Lämmitys","","Nimell.","dBA","48","49","50"]
["Kylmäaine","Tyyppi","","","","R-32","R-32","R-32"]
["","Täytösmäärä","","","kg","1.55","1.55","1.55"]
["","GWP","","","","675","675","675"]
["","Täytösmäärä","","","tCO2Eq","1.05","1.05","1.05"]
["Putkiliitännät","Neste","","Ulkohalkaisija","mm","6.35","6.35","6.35"]
["","Kaasu","","Ulkohalkaisija","mm","9.52","12.7","12.7"]
["Putkistoliitännät","Putkiston pituus","Enint.","OU - IU","m","50","50","50"]
["","Lisäkylmäainemäärä","","","kg/m","0,02 (yli 30m putkistoille)","0,02 (yli 30m putkistoille)","0,02 (yli 30m putkistoille)"]
["","Korkeusero","IU - OU","Maks.","m","30","30","30"]
["Vakiovarusteet","RZAG35B5V1B","","","","1"]
["","Installation manual","","","","1","1","1"]
["","Refrigerant charge label","","","","1","1","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1","1","1"]
["","General safety precautions","","","","General safety precautions","General safety precautions","General safety precautions"]
["","LOT10 Energy Label","","","","LOT10 Energy Label","LOT10 Energy Label","LOT10 Energy Label"]
["","Drain cap","","","","3","3","3"]
["","Drain plug","","","","1","1","1"]
["Virransyöttö","Vaihe","","","","1~","1~","1~"]
["Syöttöjännite","Taajuus","","","Hz","50","50","50"]
["","Jännite","","","V","220-240","220-240","220-240"]
["Huomautukset","","","","","(1) - Katso toimintalämpötila-alue eri piirustuksesta","(1) - Katso toimintalämpötila-alue eri piirustuksesta","(1) - Katso toimintalämpötila-alue eri piirustuksesta"]
["","","","","","(2) - Katso sähköiset tiedot eri piirustuksista","(2) - Katso sähköiset tiedot eri piirustuksista","(2) - Katso sähköiset tiedot eri piirustuksista"]
["","","","","","(3) - Sisältää fluorattuja kasvihuonekaasuja","(3) - Sisältää fluorattuja kasvihuonekaasuja","(3) - Sisältää fluorattuja kasvihuonekaasuja"]
["Vakiovarusteet","RZAG50B5V1B","","","","","1"]
["","RZAG60B5V1B","","","","","","1"]