{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":42,"n_cols":13,"rows_kept":42,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RZAG-NV1"]
[]
[]
[]
[]
["","","","","","RZAG71N7V1B","RZAG71N2V1B","RZAG100N7V1B","RZAG100N2V1B","RZAG125N7V1B","RZAG125N2V1B","RZAG140N7V1B","RZAG140N2V1B"]
["Mitat","Yksikkö","","Korkeus","mm","870","870","870","870","870","870","870","870"]
["","","","Leveys","mm","1100","1100","1100","1100","1100","1100","1100","1100"]
["","","","Syvyys","mm","460","460","460","460","460","460","460","460"]
["Paino","Yksikkö","","","kg","81","81","85","85","95","95","95","95"]
["Kompressori","Type","","","","","","Hermeettisesti suljettu swing-kompressori","Hermeettisesti suljettu swing-kompressori","Hermeettisesti suljettu swing-kompressori","Hermeettisesti suljettu swing-kompressori","Hermeettisesti suljettu swing-kompressori","Hermeettisesti suljettu swing-kompressori"]
["Toimintalämpötila-alue","Jäähdytys","Ympäristö","Min.","°CDB","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Maks.","°CDB","52","52","52","52","52","52","52","52"]
["","Lämmitys","Ympäristö","Min.","°CWB","-20","-20","-20","-20","-20","-20","-20","-20"]
["","","","Maks.","°CWB","18","18","18","18","18","18","18","18"]
["Äänen tehotaso","Jäähdytys","","","dBA","64","64","66","66","69","69","70","70"]
["","Lämmitys","","","dBA","","","","","68 (1)","68 (1)","71 (1)","71 (1)"]
["Äänenpaineen taso","Jäähdytys","","Nimell.","dBA","46","46","47","47","49","49","50","50"]
["","Lämmitys","","Nimell.","dBA","48","48","50","50","52","52","52","52"]
["Kylmäaine","Tyyppi","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Täytösmäärä","","","kg","3.2","3.20","3.2","3.20","3.7","3.70","3.7","3.70"]
["","GWP","","","","675","675","675","675","675","675","675","675"]
["","Täytösmäärä","","","tCO2Eq","2.16","2.16","2.16","2.16","2.5","2.50","2.5","2.50"]
["Putkiliitännät","Neste","","Ulkohalkaisija","mm","10","10","10","10","10","10","10","10"]
["","Kaasu","","Ulkohalkaisija","mm","15.9","15.9","15.9","15.9","15.9","15.9","15.9","15.9"]
["Putkistoliitännät","Putkiston pituus","Enint.","OU - IU","m","55","55","85","85","85","85","85","85"]
["","","Järjestelmä","Ekvivalentti","m","75","75","100","100","100","100","100","100"]
["","","","Täyttämätön","m","40","40","40","40","40","40","40","40"]
["","Lisäkylmäainemäärä","","","kg/m","Katso asennusohje","Katso asennusohje","Katso asennusohje","Katso asennusohje","Katso asennusohje","Katso asennusohje","Katso asennusohje","Katso asennusohje"]
["","Korkeusero","IU - OU","Maks.","m","30","30","30","30","30","30","30","30"]
["","","IU - IU","Maks.","m","0.5","0.5","0.5","0.5","0.5","0.5","0.5","0.5"]
["Vakiovarusteet","Installation manual","","","","1","1","1","1","1","1","1","1"]
["","Refrigerant label for F-gas regulation","","","","1","1","1","1","1","1","1","1"]
["","General safety precautions","","","","1","1","1","1","1","1","1","1"]
["","Peel off F-gas label","","","","1","1","1","1","1","1","1","1"]
["","Tie-wraps","","","","2","2","2","2","2","2","2","2"]
["Virransyöttö","Vaihe","","","","1~","1~","1~","1~","1~","1~","1~","1~"]
["Syöttöjännite","Taajuus","","","Hz","50","50","50","50","50","50","50","50"]
["","Jännite","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]
["Virta - 50&nbsp;Hz","Virta - 50&nbsp;Hz-=-Sulakkeiden enimmäisvirta (MFA)-=-A","","","A","20","20","32","32","32","32","32","32"]
["Kompressori","Tyyppi","","","","Hermeettisesti suljettu swing-kompressori","Hermeettisesti suljettu swing-kompressori"]
["Huomautukset","","","","","","","","","(1) - ENER Lot 21 mukaisesti","(1) - ENER Lot 21 mukaisesti","(1) - ENER Lot 21 mukaisesti","(1) - ENER Lot 21 mukaisesti"]